## Slide 1
ASHRAE Dallas Chapter
1/9/2024

## Slide 2: Agenda
Why Do We Balance?
Balancing Options
  Reverse Return
  Balancing Valves
    Manual vs. Automatic (Different Technologies)
System Costs
  Initial vs. Long-term
    Material Costs & T&B (Initial)
    System Efficiencies (Long-term)
Auto-Balancing & Modulation

## Slide 3: Why Balance?
Reduced water flow reduces heat transfer
Terminals furthest from the pump in unbalanced systems receive less flow resulting in reduced heat transfer
Excessive flow
  Increases pressure drop and pump energy
  Increases pump wear and noise
  Increasing water flow to 200% of coil design
    only increases heat transfer by 6% but, increases pressure drop by 400%

## Slide 4: Balancing Options
Reverse Return Piping
Manual Balancing
Automatic Flow Control Valves
Unconventional Methods
Circulating Pumps at Each Unit

## Slide 5: Reverse Return

## Slide 6: What Is A Balancing Valve?
Balancing Valves
  provide proper distribution of water flow to terminal units in the system to ensure maximum comfort with minimal energy consumption.
Improves performance of
  HVAC Systems
  Domestic Water Systems

## Slide 7: Manual Balancing Valves

## Slide 8: Automatic Flow Control Valves (Spring Type)

## Slide 9: Automatic Flow Control Valves (Diaphragm Orifice)

## Slide 10: Cost of a System - Manually Balanced
Circuit Balance Valves required at all terminal units
System needs to be rebalanced when new terminal unit(s) added
Manual Balance = No Balancing
  Balanced at 100% Design Flow
  Unbalanced at ALL Other Flows

## Slide 11: Cost of a System - Automatically Balanced
Automatic Flow Control Valves only required at terminal units
No system rebalancing needed when new terminal unit(s) brought on line.
No AFCV required on riser
AFCV dynamically adjust to maintain flow

## Slide 12: Chilled Water HVAC System Analysis
Notes: System ‘borrowed’ from an ASHRAE Journal Article

## Slide 13: System Configuration
Pumps - 2 Primary & 2 Secondary
Chillers - Inline w/ Primary Pumps
Designed flow rate – 460 gpm (230 gpm per pump)
System analyzed under three different balancing options:
  Fully Open – no balancing
  Manual balancing
  Automatic balancing

## Slide 14: Annual System Load Profile
Normal Operating Conditions:
30- 60% of system design load
System runs less than 2% of the time at full load design conditions
Notes: This is an average from ASHRAE. A generalization of total system load for 1 year for most application.

## Slide 15
Pump Curves Comparison:
Design Conditions – 100% Load
Pump operating @ 234gpm, 103ft
Pump operating @ 230gpm, 104ft
Pump operating @ 224gpm, 105ft
No Balancing
Manual Balancing
Automatic Balancing
Notes: Design Conditions means 100% flow. There are two pumps flowing 450 GPM. The graph represents pump curve for Only one of the two pumps for all the balancing options. Both the pumps selected are identical and will behave/perform similar.

## Slide 16
Pump operating @ 225gpm
Pump operating @ 197gpm
Fixed Speed Pump Curves Comparison:
Design Conditions – 90% Load
No Balancing
Manual Balancing
Automatic Balancing
Pump operating @ 222gpm
Pump Operating point moving to the left on pump curve = ENERGY SAVINGS
Notes: Design Conditions means 100% flow. There are two pumps flowing 450 GPM. The graph represents pump curve for Only one of the two pumps for all the balancing options. Both the pumps selected are identical and will behave/perform similar.

## Slide 17
Fixed Speed Pump Curves Comparison:
Design Conditions – 50% Load
No Balancing
191 GPM
Manual
182 GPM
Automatic
113 GPM
Notes: Design Conditions means 100% flow. There are two pumps flowing 450 GPM. The graph represents pump curve for Only one of the two pumps for all the balancing options. Both the pumps selected are identical and will behave/perform similar.

## Slide 18
Fixed Speed Drive
Variable Speed Drive
3,500 rpm
Eff: 75.5 %
Power: 8 hp
100% Design Flow Condition
(Manual Balancing)
3,500 rpm
Eff: 75.5 %
Power: 8 hp
230 gpm
230 gpm

## Slide 19
Fixed Speed Drive
Variable Speed Drive
3,500 rpm
Eff: 75.5 %
Power: 8 hp
100% Design Flow Condition
(Automatic Balancing)
3,500 rpm
Eff: 75.5 %
Power: 8 hp
226 gpm
225 gpm

## Slide 20
Fixed Speed Drive
Variable Speed Drive
70 % Design Flow Condition
(Manual Balancing)
3,500 rpm
Eff: 73.8 %
Power: 7.6 hp
208 gpm
3,545 rpm
Eff: 73.7 %
Power: 7.9 hp
210 gpm

## Slide 21
Fixed Speed Drive
Variable Speed Drive
70 % Design Flow Condition
(Automatic Balancing)
2,360 rpm
Eff: 75.8 %
Power: 2.5 hp
3,500 rpm
Eff: 66.3 %
Power: 6.7 hp
158 gpm
160 gpm

## Slide 22
Fixed Speed Drive
Variable Speed Drive
50 % Design Flow Condition
(Manual Balancing)
3,500 rpm
Eff: 70.5 %
Power: 7.1 hp
3,525 rpm
Eff: 70.6 %
Power: 7.3 hp
184 gpm
182 gpm

## Slide 23
Fixed Speed Drive
Variable Speed Drive
50 % Design Flow Condition
(Automatic Balancing)
3,500 rpm
Eff: 55.6 %
Power: 5.9 hp
113 gpm
115 gpm
1,420 rpm
Eff: 76 %
Power: 0.6 hp

## Slide 24: Fixed Speed Pump Operation
30% @ 3.2 hp
100% @ 4 hp
70% @ 3.8 hp
Pump Curve
3500 rpm
Automatic Balancing Valves

## Slide 25: Variable Speed Pump Operation
Pump Curve
3500 rpm
2990 rpm
2130 rpm
100% @ 3.9 hp
70% @ 2.5 hp
30% @ 0.9 hp
Automatic Balancing Valves

## Slide 26: Energy Calculations (2-Position Control Valves @ $0.10 / kwh)
% System Load | % of Operating hours | Operation Cost ($ per % of operating hours) |  |  |  | 
 |  | Fully Open No balancing | Manual Balancing |  | Automatic Balancing | 
 |  |  | Fixed Speed Pumping | Variable Speed Pumping | Fixed Speed Pumping | Variable Speed Pumping
30 | 15.25 | 2026 | 1961 | 2031 | 1088 | 1084
40 | 19.75 | 2834 | 2744 | 2828 | 1961 | 1810
50 | 21.5 | 3251 | 3169 | 3275 | 2618 | 2186
60 | 14.25 | 2228 | 2185 | 2238 | 1841 | 1777
70 | 9.50 | 1521 | 1497 | 1545 | 1307 | 997
80 | 4.00 | 652 | 644 | 672 | 586 | 459
90 | 2.25 | 372 | 368 | 370 | 350 | 289
100 | 0.50 | 83 | 83 | 82 | 82 | 82
Approx. Annual Pump Running Cost ($/year) |  | $12,967 | $12,650 | $13,041 | $9836 | $8686

## Slide 27
High psi
Low psi
Cv rate selection of Control Valve body is critical
Uniform Cv rates lead to poor rangeability and performance
Automatic Balancing Valves kick in to protect the unit from overflow

## Slide 28: Automatic Balancing Valves & Modulation
P1
P2
P3
FLOW

## Slide 29: Automatic Balancing Valves & Modulation (Control Valve = 100% Open)
P3
P2
P1
9.2 PSI
4.7 PSI
2.5 PSI
2.2 PSID
3.1 GPM
Design 3 GPM

## Slide 30: Automatic Balancing Valves & Modulation (Control Valve = 70% Open)
P3
P2
P1
15.2 PSI
3.2 PSI
2.5 PSI
0.7 PSID
2.2 GPM
Design 3 GPM

## Slide 31: Automatic Balancing Valves & Modulation (Control Valve = 20% Open)
P3
P2
P1
22.0 PSI
2.5 PSI
2.5 PSI
0.0 PSID
0.5 GPM
Design 3 GPM

## Slide 32: Conclusion
Manual balancing valves are costly to install/balance & are ineffective during the system’s lifespan
Automatic balancing valves greatly reduce T&B time/cost, eliminate overflow by reacting to system pressure fluctuations, thereby saving energy & improving comfort

## Slide 33: QUESTIONS ?